# ENGINEERING GUIDE SPECIFICATIONS

## AIR-COOLED INVERTER SCROLL VARIABLE REFRIGERANT FLOW HEAT PUMP CHILLER

### PART 1 – GENERAL

  - SUMMARY/SYSTEM DESCRIPTION/ACCEPTABLE MANUFACTURERS

- Section includes design, performance criteria, refrigerants, controls, and installation requirements for a fully inverter air-cooled scroll heat pump chiller.  The package ISHPC shall be provided as specified on the drawings.  The package ISHPC shall meet the standards referenced in this specification and meet all local codes in effect.

- The air-cooled variable refrigerant flow heat pump modular chiller may consist of multiple individual chiller modules.  The chiller module shall be available in nominal capacities of 17, 20, 33-, 40-, 50- and 60-ton systems.  All systems shall be completely factory wired and tested prior to shipment. Each module shall include a minimum of 2, 4 or 6 compressors matched to 1, 2 or 3 stainless plate and frame evaporator for increased internal redundancy.  The quantity of tube in fin air-cooled condensers coil per system shall match the number of compressors allowing each compressor to have a fully independent refrigerant circuit reducing the potential loss associated with a compromised system.  Each ISHPC to have a Digital Chiller Controller capable of independent control or plant control of up a maximum of 5 systems.  In the event of a malfunctioning circuit the chiller will continue to operate at available maximum capacity with the alarm information made available in the history of the Chiller Control or for a potential BMS. The main chiller PCB and controls shall be capable of independent operation that is needed for a simultaneous heating and cooling application.  The main PCB is capable of local and remote control from BMS System.  The chiller controls shall have an optional BACnet gateway available to help meet the programming and integration needs of third party BMS systems.

- Acceptable Manufacturers:

- LG Electronics

- (Approved Equal)

  - REFERENCES

- Unit shall be rated in accordance with AHRI (Air-Conditioning, Heating and Refrigeration Institute) Standard 550/590, latest edition and all units shall comply with current version of ASHRAE (American Society of Heating, Refrigeration, and Air-Conditioning Engineers) 90.1.

- Unit construction shall comply with ASHRAE 15 Safety Code, UL (Underwriters Laboratories) latest edition, and ASME (American Society of Mechanical Engineers) applicable codes.

- An operational test, in which the chiller is run is performed at the factory. This test checks for proper operation of fans as well as various controls and safeties, and a certificate of unit testing, indicating successful end-of-line testing is available upon request.

  - SUBMITTALS

A.	Submit shops drawings and product data in accordance with the specifications.

B.	Submittals shall include the following:

- Total Model Selection Summary for the chiller.

- Combined System Performance Information (certification is not in scope of AHRI 550-590):

- Ambient Temperature Cooling and Heating (°F)

- Cooling and Heating Capacity (Ton and MBH)

- Power for Cooling and Heating (kW)

- EER and COP (Btu/Whr and W/W)

- NPLV (Cooling Only Btu/Whr)

- Water Temperature Cooling and Heating (in/out °F)

- Fluid Flow Rate Cooling and Heating (GPM)

- Pressure Drop Cooling and Heating (ftAq)

- Individual Chiller Specifications to include:

- Dimensions (width, height and length)

- Weight (lb)

- Refrigerant Type, # of circuits and amount required per circuit

- Sound Data in accordance with AHRI Standard 370-2015

- Sound Power Cooling and Heating

- Sound Pressure Cooling and Heating (5 feet and 30 feet)

- Compressor Type and Quantity

- Oil Type and Oil Charge (oz)

- Evaporator Type, Flow Rate Cooling and Heating, Connection (Size/ Type) and Pressure Drop (ftAq)

- Fan Motor Type, Flow (CFM) and Power (W)

- Dimensioned plan and elevation view drawings and location water connections size and type.

- Electrical Specifications to include Model, Voltage, Phase, Maximum Fuse Amps (MFA) or Maximum Circuit Breaker Amps, Minimum Circuit Amps (MCA), Running Load Amps (RLA), Minimum Start Current (MSC) and Quantity of Independent Circuits.

- Enhance Sound Information for Cooling and Heating tested in accordance with AHRI Standard 370-2015 (data based on individual unit installation).  Only provide full load performance in Heating: charts provided in for Cooling and Heating Mode.

| Model | Octave bands, Hz (Sound Power dBA) |  |  |  |  |  |  |  |  |  |  |  |  | Overall A-Weighted Load |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 63 | 125 | 200 | 250 | 500 | 1000 | 1250 | 2000 | 2500 | 4000 | 5000 | 8000 | 10000 | 100% | 75% | 50% | 25% |

| Model | Octave bands, Hz (Sound Pressure 5 Feet dBA) |  |  |  |  |  |  |  |  |  |  |  |  | Overall A-Weighted Load |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 63 | 125 | 200 | 250 | 500 | 1000 | 1250 | 2000 | 2500 | 4000 | 5000 | 8000 | 10000 | 100% | 75% | 50% | 25% |

| Model | Octave bands, Hz (Sound Pressure 30 Feet dBA) |  |  |  |  |  |  |  |  |  |  |  |  | Overall A-Weighted Load |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 63 | 125 | 200 | 250 | 500 | 1000 | 1250 | 2000 | 2500 | 4000 | 5000 | 8000 | 10000 | 100% | 75% | 50% | 25% |

- Single-line schematic diagram of line voltage and control system indicating points for field interface/connection.

- AHRI 550-590 Cooling Performance Data Page to include:

- Unit information

  - Model

  - Power Supply (phase, # of wires and volts)

  - Refrigerant Type

  - Cooling Capacity (Ton)

  - Quantity of Compressors

  - Dimensions (length inch, height inch and width inch)

  - Operating Weight (lb)

  - Shipping Weight (lb)

  - Refrigerant Charge (lb)

  - Sound Pressure (AHRI Standard 370-2015 5 Feet and 30 Feet)

- Cooling Performance Data

- System KW (W/O Pump)

- EER (Btu/Whr)

- Full Load Power Input per Ton (kW/usRT)

- NPLV (Btu/Whr)

- 100% EER (Btu/Whr)

- 75% EER (Btu/Whr)

- 50% EER (Btu/Whr)

- 25% EER (Btu/Whr)

- Evaporator Data

  - Heat Exchanger Structure

  - Fluid Type and % of Glycol

  - Water Connection (Size and Type)

  - Fouling Factor (h·ft²·°F/Btu)

  - Entering Water Temp (°F)

  - Leaving Water Temp (°F)

  - Flow-rate (GPM)

  - Pressure Drop (ftAq)

- Condenser  Data

- Heat Exchanger Structure

- Refrigerant Type

- Altitude (ft above sea level)

- Number of Fans

- Total Air Flow Each (CFM)

- Entering Air Temperature (DBT °F)

- Heating Performance  (Tested in accordance with AHRI 550-590 Procedure- not in certification scope of standard)

- Unit information

      - Model

      - Power Supply (phase, # of wires and volts)

      - Refrigerant Type

      - Heating Capacity (MBH)

      - Quantity of Compressors

      - Dimensions (length inch, height inch and width inch)

      - Operating Weight (lb)

      - Shipping Weight (lb)

      - Refrigerant Charge (lb)

      - Sound Pressure (AHRI Standard 370-2015 5 Feet and 30 Feet)

- Heating Performance Data

- System KW (W/O Pump)

- COP (W/W)

- Evaporator Data

      - Heat Exchanger Structure

      - Fluid Type and % of Glycol

      - Water Connection (Size and Type)

      - Fouling Factor (h·ft²·°F/Btu)

      - Entering Water Temp (°F)

      - Leaving Water Temp (°F)

      - Flow-rate (GPM)

      - Pressure Drop (ftAq)

- Condenser  Data

- Heat Exchanger Structure

- Refrigerant Type

- Altitude (ft above sea level)

- Number of Fans

- Total Air Flow Each (CFM)

- Entering Air Temperature (DBT °F)

  - QUALITY ASSURANCE

- Qualifications: Equipment manufacturer must specialize in the manufacturing of the products specified and have a minimum of five years of experience with the type of equipment and refrigerant offered.

- Regulatory Requirements: Comply with the codes and standards specified. Heat Pump Chiller manufacturer's plant must be ISO registered.

  - DELIVERY, STORAGE, AND HANDLING

- The Heat Pump Chiller shall be delivered with condensing section completely assembled and refrigerant charge matching the name plate.

- Comply with manufacturer's installation instructions for rigging, unloading, and transporting the heat pump chiller modules.

  - LIMITED PART ONLY WARRANTY

- All parts of a qualified system are warranted for a period ending on the earlier to occur of (12) months after the date of original commissioning or eighteen (18) months from ship date of manufacturer. The compressor part only is warranted for an additional (24) month period from the established warranty start date as part of the Limited Part Only Warranty.  The limited parts only warranty period, including all parts and the compressor, may be extended to a total of (60) months or up to (120), months in (12) month increments, by the purchase of additional warranty period increments, which may be only purchased at the time of the original chiller equipment purchase.

- The qualified system must be commissioned by an individual or company that has successfully completed LG’s Chiller System Commissioning and Service training and holds a current government issued license that authorizes that individual or company to service and install HVAC equipment in the state where the chiller is located, if applicable.  The system must also be commissioned per the applicable published documents.  Service and maintenance of the chiller must also be performed by a qualified individual, as provided in the limited warranty statement.

- Maintenance of the heat pump chiller equipment while under warranty is mandatory and shall be performed in accordance with the applicable published instructions provided within the installation and operation manual.  Proper fluid condition is to be maintained per the installation and operation manual during the warranty period.  Annual testing repots and documentation shall be stored and made available upon request by the manufacturer as part of the owner’s responsibility and is required under the Limited All Parts Only Warranty.

### PART 2 – PRODUCTS

2.1	INVERTER SCROLL HEAT PUMP CHILLER DESCRIPTION

- Provide and install as detailed on plans Factory-assembled, single-piece air-cooled variable refrigerant flow liquid heat pump chiller(s) in the quantity required. Contained within the unit cabinet shall be all factory wiring, piping, controls, refrigerant charge (R-410A), and special features prior to field start up.

- The heat pump chiller shall be functionally tested at the factory to ensure components including sensors, wiring, electronics, and microprocessor controls and their function.

- Chiller shall be heat pump and provide both hot and cold water.  Remote mode change option shall be required.

- Each outdoor unit refrigeration circuit shall include, but not limited to the following components:

- Refrigerant strainer(s)

- Check valve(s)

- Inverter driven, medium pressure vapor injection, high pressure shell compressors

- Oil separator(s)

- Accumulator /controlled volume receiver(s)

- 4-way reversing valve(s)

- Vapor injection valve(s)

- Oil Level sensor(s)

- Electronic expansion valve(s)

- Sub-cooler (s)

- Vapor Injection Valve(s)

- High and low side Schrader valve service ports with caps

- Shared brazed plate water to refrigerant heat exchanger with (4) refrigerant connections and (2) water connections, 316 stainless steel construction with (2) refrigerant circuits and a single water circuit, heat exchanger refrigerant circuits shall be rated to 650 PSIG, water circuit rated to 340 PSIG.

2.2	DESIGN AND PERFORMANCE REQUIREMENTS

  - General: The unit shall be in accordance with the standards referenced in section 1.2 and any local codes in effect.

  - The ISHPC shall have Certified AHRI 550/590 Cooling Performance of 19.46 IPLV and a full load EER of 10.32.

  - Performance: Refer to the schedule of performance as noted in contract documents.  The heat pump chiller shall be capable of stable operation to a minimum percentage of 20% of rated capacity of full load.

  - Operating Range: The heat pump chiller shall have the ability to control leaving chilled fluid temperature from 14°F to 68F in cooling and 86°F to 131°F in heating. Unit shall be capable of starting and running at outdoor ambient temperatures from 5°F to 125°F in cooling and -22°F to 95°F in heating mode without additional accessories.

  - Low ambient cooling down to 5°F without the need for field installed additional factory installed accessories.

  - Heating performance to be capable of providing 120°F Leaving Water down to 32°F providing 100% of high temp tested heating capacity per ASHRAE 90.1.

  - Acoustics: Sound pressure level measured in accordance with ISO 3745 Standard for anechoic room rated conditions. The manufacturer shall provide the necessary sound treatment if required to comply with a maximum sound pressure of 56 dBA for both cooling and heating mode based on an A-Weighted Test at 30 feet and 76 dBA at 5 feet A-Weighted Test in accordance with ANSI/AHRI Standard 370-2015. Sound data shall be based on individual unit installation and report to comply with section 1.3.B.6 of this document.

  - The maximum acceptable A-Weighted ANSI/AHRI Standard 370-2015 rated sound pressure performance at 30 feet shall be:  Cooling Mode 56 db(A) and Heating Mode 60 db(A) per individual module.

  - Each refrigeration circuit shall contain a 316 stainless steel brazed plate fluid heat exchanger and EEV for sub-cooling and vapor injection operations.  All heat exchangers shall maintain independent refrigerant circuits and shall not exceed a combined capacity of 20 tons.

  - INVERTER chiller-heat pump shall be provided with a factory installed fusible plug or rupture disc.

  - Outdoor fan motors shall be BLDC type motors.  Speed is to vary based on target refrigeration pressure that will vary based on mode and ambient condition.  Targets are determined by internal heat pump chiller control logic.

2.3	HEAT PUMP CHILLER COMPONENTS

- MATERIALS OF CONSTRUCTION

  - The base must be able to withstand concentrated load. The base must be installed with a maximum gradient of 1/300 inches. The mounted height of the base must be higher than the surface of the fluid or snow and drain holes must be installed around. The height of the base must be set according to the installation environment so that the product is not submersed in fluid or snow.

  - The default height of the base is 4 inches.  The average accumulation of snow fall for area of installation shall be added to the minimum 4” base height.

  - The casing shall be constructed so that is easy to disassemble and assemble during            maintenance/repair. It shall be insulated to prevent condensation, and structurally sound to prevent vibration and/or abnormal noise.

  - Exterior panels shall have an epoxy coat with a salt spray rating of up to 500 hours.

- COMPRESSOR/COMPRESSOR COMPONENTS AND SEQUENCE OF OPERATION

  - The R-410A Compressor shall be a hermetic, high-side shell (HSS), commercial grade, compliant scroll direct-drive design.  Compressor shall be designed and assembled by the INVERTER chiller-heat pump manufacturer specifically for use in the air source INVERTER chiller-heat pump product line. Third party manufactured, branded, or designed to the INVERTER chiller-heat pump system’s OEM specifications by a third-party manufacturer shall not be acceptable.

  - Compressor Design: The compressor design shall be of the high-pressure shell scroll type where the internal pressure below the scroll plates of the compressor shall be at the same high pressure and high temperature. The motor shall be cooled by high pressure gas at temperatures above saturation conditions and minimize the mixing of refrigerant liquid with oil in the sump. The system shall employ a high-pressure oil return method returning recovered oil from the oil separator directly into the oil sump of the compressor; oil shall not be allowed to return via the suction line. Bearing surfaces are continually coated with oil. The compressor shall employ an Aero-bearing constructed with high lubricity materials increasing operation time in case of low sump oil level.  The fixed and oscillating compressor scroll components shall be made of high grade (GC25) or denser steel material. All scrolls shall be heat treated and tempered. The oscillating scroll shall be finely machined and polished. PVE refrigerant oil shall be used as the sole liquid used to maintain a seal between the high and low sides of the compression chamber. Compressors that require the use of any type of mechanical or wearable sealant material between the moving surfaces of the compression chamber is NOT ACCEPTABLE.

  - Single frame systems will have 2 inverter compressors, Double Frame systems will have 4 inverter compressors and Triple Frame systems will have 6 compressors.  Each compressor has a nominal capacity of 10 tons.

  - Each refrigeration circuit shall employ a single inverter compressor with a maximum refrigerant charge not to exceed 15.4 lbs.

  - All compressors shall employ high pressure oil return directly into the compressor oil sump. Oil return via the suction line shall not be permitted.

  - All compressors shall provide, during off cycle, a trickle charge to the windings to keep oil warm. External crankcase heaters shall not be permitted.

  - All inverter driven compressors within a frame are to operate in unison at the same level. Staging of compressors shall not be permitted with in a frame.

  - Compressor shall soft start via inverter and shall load only to the required load.  Compressors start current for 208-230V the minimum start current shall not exceed 25% of MCA and the 460V the minimum start current shall not exceed 20% of MCA.

  - The system design is to have a shared evaporator between 2 compressors.  System is design to run on any active compressor that are not offline from an error code.  External human interface shall not be acceptable if required for emergency operation.  Compressor Error messages are available from Main PCB for BMS interface.  Local HMI or Chiller Control shall also keep record of compressor error codes as a redundant feature.

  - Vibration prevention isolation rubber grommets shall be installed to isolate compressor from base frame.

  - Inverter Compressor Control and Sequence:  Each compressor shall be equipped with a dedicated inverter compressor drive. The control of multiple compressors using a single drive shall not be acceptable. The frequency variable boundary of inverter scroll compressor shall be minimum 30Hz and maximum 127Hz.  The inverter driver controller shall be matched with the physical properties of the compressor. The drive shall be manufactured by the INVERTER chiller-heat pump unit manufacturer. The inverter drive and matching compressor shall have been thoroughly tested as a matched pair. The inverter drive shall be programmed to avoid operating the compressor at any speed that results in harmonic vibration, nuisance noise, or mechanical damage to either the driver or the compressor with power provided that is within the tolerance specification.  The compressor inverter drive assembly and software must be designed, manufactured, and supplied by the INVERTER chiller-heat pump product manufacturer. Third party branded inverter driver hardware and/or driver software or inverter driver hardware and/or software provided by a third-party manufacturer to meet OEM specifications shall not be allowed.  All inverter drive hardware or software manufactured in, is a product of, or sourced from China, or using a broker or third-party provider as an intermediary that obtains the product from CHINA shall not be acceptable.

  - Hot Gas Bypass: Includes factory-mounted hot gas bypass valve, solenoid valve, for each circuit.

  - Inverter Compressor Refrigerant Flow Control Requirements:  An active refrigerant -in-circulation control system consisting of a refrigerant storage container, interconnecting refrigerant piping control valves, pressure transducers, microprocessor control, and software to continuously monitor necessary refrigeration cycle operating parameters to maintain stable cycle operation between minus (-)22°F and 122°F ambient conditions. The refrigerant system operating conditions shall be checked by the algorithm at three-minute intervals and if needed automatically and dynamically remove and store refrigerant to the storage tank or inject refrigerant from the tank into the refrigerant circuit.   The algorithm shall adjust the needed refrigerant with input:

      - As the outdoor air temperature changes.

      - System mode of operation changes.

      - The path of refrigerant flow through the outdoor coil is modified.

      - The system's target suction and head pressure control values are adjusted.

  - Maximum Hz operation shall be capable of being set at local control or external connection to Unit Main PCB.  When educe capacity and or load shedding is desired.

  - In an event of low load application, below 20% of full rated capacity, an alternating operation should allow for uniform average operation time for each compressor.

  - Oil Management:  The system shall utilize a high-pressure oil return system to ensure a consistent film of oil on all moving compressor parts at all points of operation. Oil is returned to compressor through a separate high pressure oil injection pipe directly into the oil sump. Oil returned to the compressor via the suction port of the compressor shall not be allowed.  Each compressor shall be provided with a high efficiency independent centrifugal cyclone type oil separator, designed to extract oil from the oil/refrigerant gas stream leaving the compressor.  The system shall have an oil level sensor in the compressor to provide direct oil level sensing data to the main controller. The sensor shall provide data to main outdoor unit PCB to start oil return mode.  The system shall only initiate an oil return cycle if the sensed oil level is below oil level target values as determined by the microprocessor. The system shall display an error if the oil sensor signals low oil level for a period of 130 minutes or longer.  A default oil return algorithm shall automatically initiate the oil return mode if the system detects a failure of the oil sump sensor. A fault code shall be reported by the system.  Timed oil return operations or systems that do not directly monitor compressor oil level shall not be permitted.

  - Vapor Injection Requirement and Description:  System shall have a medium pressure gas vapor injection function employed in the heating and cooling modes to increase system capacity when the outdoor ambient temperatures are low and to lower compressor lift when temperatures are high. The compressor vapor injection flow amount shall be controlled by the vapor injection sub-cooling algorithm reset by discharge gas temperatures of the compressor.  Pressure differential design shall draw oil from the compressor sump reservoir, pressurize the oil and inject the oil directly to the crankshaft journals maintaining a consistent film of oil between all moving parts. Auxiliary, indirect, or electronically driven oil pumps are not acceptable.  The viscosity property of the PVE oil in the compressor sump shall be maintained regardless of compressor operation and the surrounding ambient temperature.  The compressor shall be equipped with control to automatically supply the compressor windings with a trickle charge of electricity enough to maintain the oil temperature above the refrigerant boiling temperature that is automatically activated only when the ambient temperature is below 40F, and the compressor is not running. Addition of external crank case heaters shall not be allowed.  Low side shell (LSS) type compressors that use suction vapor to cool the compressor motor shall not be allowed.

  - Vapor Injection Sub-cooler:  Each compressor circuit shall a factory provided and mounted sub-cooler assembly consisting of a brazed plate type sub-cooling heat exchanger and EEV providing refrigerant sub-cooling modulation control by fuzzy logic of EEV and by mode of operation to provide capacity and efficiency as required. Brazed plate shell & tube heat exchangers shall not be allowed for this function.

  - Internal Compressor Cooling Requirements and Description:  The motor winding insulation shall be designed to operate continuously at a minimum temperature of 180°F without deterioration.  The motor cooling system shall be designed to always maintain acceptable operational temperature and, in all conditions, using high pressure, hot refrigerant vapor as motor coolant.  Low side shell (LSS) and compressors that use low pressure, low temperature refrigerant gas to cool the motor shall not be allowed.

  - Active Refrigerant Volume Management:  The INVERTER chiller-heat pump system shall be able to operate at all published conditions in cooling or heating mode without the need of adding or removing refrigerant from the system.  The air source unit shall be provided with an isolated vessel, interconnecting piping, valves, and sensors to store refrigerant and actively pass refrigerant to (or from) the refrigerant circuit in real time as necessary to maintain stable refrigeration cycle operation.  The air source unit microprocessor shall be provided with an algorithm that monitors the INVERTER chiller-heat pump system head pressure, suction pressure, sub-cooling, superheat, compressor speed, high and low side temperatures, chilled water temperatures, hot water temperatures, status of water flow and the load on the system at three minute intervals and if needed, automatically and dynamically remove and store refrigerant to the storage tank or inject refrigerant from the tank into the refrigerant circuit.  INVERTER chiller-heat pump systems that cannot perform active refrigerant control are not acceptable.

  - Compressor are designed to operate independently.  Unless the error code interrupts control power the error of compressor will be broadcasted to BMS front end, and the remaining compressors normal operation is not interrupted.

- FLUID HEAT EXCHANGERS

  - The fluid heat exchanger shall be a 316 stainless-steel plate and frame type heat exchanger.

  - As standard, the fluid heat exchanger shell and fluid piping in the chiller heat pump shall be insulated with rigid poly styrene, 1 1/4” thickness and black color.

- AIR COOLED HEAT EXCHANGER

  - The air-cooled heat exchange arrangement shall be 3-row, 14 FPI (fins per inch), 48 rows.  Use wide louvered aluminum fin. The coil(s) shall be sized to provide full heat rejection at a maximum 125°F or -22F minimum ambient temperature for 460V chiller heat pumps and 122°F or -22F for 208-230V chiller heat pumps both at sea level.

  - The coil(s) shall be factory tested to a minimum 600 psig.

  - Air Cooled heat exchanger shall include “black fin II” coating, a heavy anti-corrosion treatment protecting the heat exchanger from high salinity, humidity, and pollution.  The coating is applied to the fin stock only and the corrosion performance is compliant to meet a 10,000-hour rated salt spray performance test that is conducted in accordance with ASTM B117 standard.

  - ISO 21207 Salt Spray Test Method B – 10,000 hours performance compliant.

  - ASTM B-117 Acid Salt Test – 900 hours performance compliant.

  - The Black Fin II coating shall be certified by Underwriters Laboratories and per ISO 21207.

  - Air Cooled heat exchanger shall be used with 99.9% purity or above phosphorus deoxidized copper without joint and it shall be constructed with Pre-Coated Aluminum fins that are mechanically bonded to increase the thermal transfer surface area.  (Cross fin and tube type).

  - Fan(s) shall be connected directly to driving motor. Motor shall be BLDC type that can increase efficiency. The fan motors shall vary speed to maintain refrigeration head pressure.

  - Fan design at rated cooling capacity shall not exceed 90% of full or maximum RPM/Hz.

  - System is capable of low noise operation and can reduce sound by up to 3 db.

- ELECTRONIC EXPANSION VALVES

  - EEV’s shall be used during adiabatic-expansion process within the refrigerant cycle to expand high pressure liquid refrigerant at both the Air-cooled heat exchanger and the fluid heat exchanger exit thereby converting to low temperature/low pressure state.

  - LEV’s (linear expansion valves) shall be activated to adjust refrigerant amount according to fluid heat exchanger load during cooling operation.

  - Based on data from various sensors installed in the chiller heat pump, the micro-processor shall be able to analyze operation status of the system and compressor shall control the optimum refrigerant amount linearly.

  - By applying electric pulse signal (up to 2,000 pulses) to the stepping motor, it shall be able to adjust refrigerant flow and superheat and sub-cooling.

- CONTROL SYSTEM

  - Controller shall operate to control the overall system at optimal condition with a micro-computer unit installed in the chiller heat pump, and be able to control electronic expansion valve and inverter driven compressor(s) based on the 4 measured values: suction gas pressure, discharge gas pressure, discharge gas temperature, and heat exchanger refrigerant temperature

  - Control system shall include sensor(s) functionality connected to the heat pump chiller and the varying operation mode status.

  - Heat Pump Chiller shall be equipped with self-protection devices and system protection functionality.

  - Internal flow switch is included as standard, installed, and wired.

  - External contact closure indicating pump operation is required and is to be hard wired to heat pump chiller main PCB.

  - Continued heat operation during defrost is required on systems that are at or above 33 tons or double and triple frame modules.

  - Target Evaporator temperature is set based on leaving water temperature allowing for energy savings as leaving water temps settings can change with the application and time of day.

  - If the unit is off and not running due to error the service tool provided by the manufacture shall be capable of downloading the last 180 seconds of operational time the chiller was running helping to diagnose field service issues that may arise.

- HEAT PUMP CHILLER UNIT CONTROLLER AND DISPLAY (HMI- HUMAN MACHINE INTERFACE)

  - The HMI control interface can be applied for simple product control.  Relocation & re-installation of HMI controller shall be possible.

  - The HMI may be relocated up to 1500 wire feet away from chiller heat pump.

  - Black box function shall retain the last 180 seconds of operational data prior to a failure.

  - Scheduled operation shall be possible via the HMI.

  - High ambient control box for operation in ambient temperatures to 125°F (52°C).

  - The controller shall be equipped with a cycle indication display to directly monitor refrigerant pressure conditions for refrigerant cycle and high-pressure gas safety management.

  - Chiller heat pump interface controller/HMI shall be capable of networking up to 5 chiller heat pump modules and control & monitor up to five (5) chiller heat pumps as one system if desired.  For systems larger than five modules several parallel networks of up to five modules may be installed and controlled via BMS. Up to 99 parallel systems are capable of being controlled by a third party BMS.

  - Optional Heat Pump Chiller Control BACnet Gateway.  The Control Gateway shall include Niagara4.7 or later based hardware, with a minimum 512 MB DDR SDRAM, 2GB total eMMC flash storage with user space set at 1GB, 1 RS485 port, 2 10/100 MB Ethernet ports, with BACnet and Modbus network protocol capability.  Standard interface is BACnet/IP.  BACnet/MSTP is an optional solution and should be specified if needed.

- WATER PIPING AND FLOW REQUIREMENTS:

  - The heat pump chiller is to be capable of a minimum flow is at a 20-degree delta between entering and leaving water and maximum flow capable of a 4-degree delta between entering and leaving water temperatures.

  - The heat pump chiller is provided with a factory installed flow switch that is prewired as a required safety circuit for operation.

  - A strainer (50 Mesh or above) shall be provided, by others, and installed in the supply fluid piping to each module to prevent solid bodies or particles from entering the fluid heat exchanger. Strainer shall be installed on leveled pipe and shall be serviceable by individual manual isolation valves, by others, that permit each strainer to be removed and allowing the remaining modules to continue to operate.

  - Flexible joints shall be installed at the inlet and outlet pipes of each module.

  - Fluid piping and needed insulation shall be properly specified by engineer and be compliant per local code for both process and comfort cooling applications.

  - Piping is to be installed and service valves provided so that each heat pump chiller module shall have service valves and the isolation of an independent module in the array shall not affect the flow and operation of the additional heat pump chiller modules that work together to create the heat pump chiller plant.  On a four-pipe system this is required for both hot and cold water.

  - Maximum water pressure design for the system is 142 psi.

  - All water piping and accessories to be independently supported from the equipment and the dead weight of the pipe or accessories is not transmitted or supported by the equipment in any way.

  - The following fluid specification shall be maintained; Water- PH 7-9, total dissolved solids less than 1000PPM, hardness (CaCo3) 30-500 PPM, alkalinity (CaCo3) 0-500 PPM, chlorides less than 200 PPM, sulfates less than 200 PPM. Water with 25% glycol- PH 7-9, total dissolved solids 1000 -10,000 PPM, conductivity 1000-5000 PPM, hardness (CaCo3) 30-500 PPM, alkalinity (CaCo3) more than 500 PPM, chlorides less than 200 PPM, sulfides less than 200 PPM. Other fluid conditions shall be as defined in specifications provided elsewhere.