Guide Specifications

# PRODUCT(S) – Outdoor Units (Multi Zone Systems)

## Multi F and Multi F with LGRED˚	 <LMU183HV><LMU243HV> <LMU303HV><LMU363HV><LMU180HHV><LMU240HHV><LMU300HHV>

### Product Design

#### The multi zone HVAC system available as a Multi F and Multi F with LGRED˚ system shall be a variable capacity, direct expansion (DX) heat pump engineered system consisting of a single outdoor unit and at least two indoor units. The outdoor unit shall have a single inverter compressor. The outdoor unit shall be connected to multiple indoor units (ducted, non-ducted or mixed type) through a network of piping and control wiring. Each indoor unit shall be capable of providing individual control.

#### The LG Multi F heat pump system shall be an air cooled system consisting of a single outdoor unit connected to multiple indoor units. All indoor units shall be in the same mode (heating or cooling) at the same time.

#### The heat pump system will be available in 208/230V, 60Hz, 1 phase.

### Operating Conditions

#### The outdoor unit shall be capable of the following ambient operating range

##### Multi F <LMU183~363HV>

###### Cooling: 14°F DB to 118°F DB <with optional low ambient kit from -4°F DB to 118°F DB>

###### Heating: -4°F WB to 68°F WB

##### Multi F with LGRED° <LMU180~300HHV>

###### Cooling: 14°F DB to 118°F DB <with optional low ambient kit from -4°F DB to 118°F DB>

###### Heating: -13°F WB to 75°F WB

### General Features

#### Unit shall be manufactured by LG.

#### The air-conditioning system shall use R410A refrigerant.

#### The system shall have one air source outdoor unit.

#### Refrigerant circuit for Multi F <LMU183 ~363HV> and Multi F with LGRED° <LMU180~300HHV> multiple piping system

##### The refrigerant circuit shall be field piped to multiple (ducted, non-ducted or mixed) indoor units to effectively and efficiently control the heating or cooling operation of the multi zone system.

##### All refrigerant piping from outdoor unit to indoor units shall be field insulated.

#### Factory installed microprocessor controls in the outdoor unit and indoor units shall perform functions to efficiently operate the multi zone system and communicate in a tree configuration from outdoor unit to indoor units via minimum 14 AWG, 4 conductor and stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### The Multi F and Multi F with LGRED° multiple piping system shall have the ability to connect 2 <LMU183HV, LMU180HHV>, 2 to 3 <LMU243HV, LMU240HHV> or 2 to 4 <LMU303~363HV, LMU300HHV> indoor units.

#### The system shall be capable of performing continuous operation even when power is turned off to an individual indoor unit.

#### The outdoor unit shall be internally assembled, wired and piped from the factory.

#### The factory assembled system shall have the outdoor unit fitted with refrigerant strainer, check valves, oil separator, accumulator <LMU303~363HV, LMU180~300HHV>, 4-way reversing valve, electronic expansion valve(s), high side and low side refrigerant charging ports, and a service port.

### Field Supplied Refrigerant Piping Design Parameters

#### The outdoor unit shall be capable of operating at an elevation of 49.2 feet above or below the indoor units.

#### The outdoor unit shall be capable of operating with up to 164 feet <LMU183HV, LMU180HHV>, 230 feet <LMU243HV>, 246 feet <LMU303~363HV, LMU240~300HHV> of total equivalent refrigerant piping length.

#### The outdoor unit shall be capable of operating with up to 82 equivalent feet of refrigerant piping length to the farthest indoor unit.

### Defrost Operations

#### The outdoor unit shall be capable of auto defrost operation to melt accumulated ice off the outdoor unit heat exchanger. The defrost cycle control shall be based on outdoor ambient temperatures and outdoor unit heat exchanger temperatures.

#### The <LMU183 ~363HV> shall accommodate an optional drain pan heater.  The <LMU180~300HHV> shall include a factory installed drain pan heater.

### Oil Management

#### The outdoor unit shall have an oil injection mechanism to ensure a consistent film of oil on all moving compressor parts at low speed.

#### The outdoor unit shall have an oil separator to separate oil mixed with the refrigerant gas during compression and return oil to the compressor.

### Fan and Motor Assembly

#### Each outdoor unit shall be equipped with one direct drive variable speed propeller fan with Brushless Digitally Controlled (BLDC) motor with a horizontal air discharge.

#### The fan blades shall be made of Acrylonitrile Butadiene Styrene (ABS) material.

#### The fan(s) shall be equipped with permanently lubricated bearings.

#### The fan motor(s) shall have variable speed to a maximum of 840 RPM <LMU183 ~243HV>, 750 RPM <LMU303 ~363HV>, 950 RPM <LMU180~300HHV>.

#### The fan(s) shall have a raised guard to help prevent contact with moving parts.

### Cabinet

#### The outdoor unit cabinet shall be made of pre-coated metal (PCM).

#### The front/side panels of the outdoor unit shall be removable type for access to internal components.

#### Outdoor unit cabinet shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.

### Outdoor Unit Coil

#### The outdoor unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### The aluminum fins shall have factory applied corrosion resistant GoldFin™   material.

#### Coil coating shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.

#### The outdoor unit coil shall be factory tested to a pressure of 600 psig.

#### The coil for each outdoor unit shall have a minimum of 14 Fins per Inch (FPI).

#### The coil for each outdoor unit shall have a 2 row heat exchanger.

#### The outdoor unit cabinet shall have a coil guard.

### Compressor(s)

#### The outdoor unit shall be equipped with one hermetically sealed, digitally controlled, inverter driven twin-rotary compressor.

#### The inverter driven, digitally controlled compressor shall be capable of operating in a frequency range from 10 Hz to 99 Hz <LMU183 ~363HV>, 20 Hz to 100 Hz <LMU180~300HHV> with control in 1 Hz increments.

#### The compressor shall be mounted on vibration attenuating rubber grommets.

#### The compressor shall use a factory charge of Polyvinyl Ether (PVE) oil.

#### The compressor bearing(s) shall have Teflon™ coating.

#### The compressor shall be equipped with over-current protection.

### Operational Sound Levels

#### The outdoor unit shall have sound levels not exceeding 54 dB(A) <LMU183~363HV, LMU180HHV>, 55 dB(A) <LMU240~300HHV>, tested in an anechoic chamber under ISO 3745 standard.

### Sensors

#### The outdoor unit shall have

##### Suction temperature sensor

##### Discharge temperature sensor

##### High pressure sensor

##### Low pressure sensor

##### Outdoor temperature sensor

##### Outdoor unit heat exchanger temperature sensor

### Wind Load Installations for Outdoor Units

#### Provide Florida wind Load Installation Drawings that meet the requirements of the 2020 Florida Building Code, 7th Edition and ASCE Standard 7-2016 with submittal.

### Warranty

#### Limited Warranty Period

##### STANDARD FIVE (5) YEAR WARRANTY FOR A QUALIFIED SYSTEM - The Part(s) of a qualified System, including the compressor, are warranted for a period (the “Standard Parts Warranty Period”) ending five (5) years after the date of original installation. In absence of proof of installation the warranty date will end five (5) years from the date of manufacture.

##### ADDITIONAL TWO (2) YEAR COMPRESSOR PART WARRANTY - The Compressor is warranted for an additional two (2) year period after the end of the applicable Standard Part Warranty Period (the “Compressor Warranty Period”).

#### Extended Warranty

##### The Standard Warranty Period and the Compressor Warranty Period are extended to a total of ten (10) years (the “Extended Warranty Period”) for qualified Systems that have been (a) installed by a party that has completed the Training Requirements, (b) installation is pursuant to LG’s published instructions, and (c) product is registered within 60 days of startup at www.lg-dfs.com or www.lg-dfs-warranty.com.

## Multi F Max and Multi F Max with LGRED˚ <LMU481HV><LMU541HV><LMU601HV> <LMU361HHV><LMU421HHV><LMU480HHV>

### Product Design

#### The multi zone HVAC system available as a Multi F Max and Multi F Max with LGRED˚ system shall be a variable capacity, direct expansion (DX) heat pump engineered system consisting of a single outdoor unit and at least two indoor units. The outdoor unit shall have a single inverter compressor. The outdoor unit (Multi F Max) shall be connected to multiple indoor units (ducted, non-ducted or mixed type) through a Branch Distribution Unit (BDU) connected to a network of piping and control wiring. Each indoor unit shall be capable of providing individual control.

#### The LG Multi F heat pump system shall be an air cooled system consisting of a single outdoor unit connected to multiple indoor units through a Branch Distribution Unit (BDU). All indoor units shall be in the same mode (heating or cooling) at the same time.

#### The heat pump system will be available in 208/230V, 60Hz, 1 phase.

### Operating Conditions

#### The outdoor unit shall be capable of the following ambient operating range

##### Multi F MAX <LMU481HV><LMU541HV<LMU601HV>

###### Cooling: 14°F DB to 118°F DB <with optional low ambient kit from -4°F DB to 118°F DB>

###### Heating: -4°F WB to 68°F DB

##### Multi F MAX with LGRED° <LMU361HHV><LMU421HHV><LMU480HHV>

###### Cooling: 14°F DB to 118°F DB <with optional low ambient kit from -4°F DB to 118°F DB>

###### Heating: -13°F WB to 75°F DB

### General Features

#### Unit shall be manufactured by LG.

#### The air-conditioning system shall use R410A refrigerant.

#### The system shall have one air source outdoor unit.

#### Refrigerant circuit for Multi F MAX <LMU481HV><LMU541HV><LMU601HV> and Multi F MAX with LGRED° <LMU361HHV><LMU421HHV><LMU480HHV> branch distribution piping system

##### The refrigerant circuit shall be field piped with manufacturer supplied Branch Distribution (BD) unit(s) and Y-branches (if applicable) to multiple (ducted, non-ducted or mixed) indoor units to effectively and efficiently control the heating or cooling operation of the multi zone system.

##### All refrigerant piping from outdoor unit to BD unit and from BD unit to indoor units shall be field insulated.

#### Factory installed microprocessor controls in the outdoor unit, BD Unit and indoor units shall perform functions to efficiently operate the multi zone system and communicate in a tree configuration from outdoor unit to BD unit via minimum 14 AWG, and BD unit to indoor units via minimum 14 AWG, 4 conductor, stranded,  shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### The Multi F MAX <LMU481HV><LMU541HV><LMU601HV> and Multi F MAX with LGRED° <LMU480HHV> branch distribution piping system shall have the ability to connect 2 to 8 indoor units, the Multi F MAX with LGRED° <LMU361HHV> branch distribution piping system shall have the ability to connect 2 to 5 indoor units and the Multi F MAX with LGRED° <LMU421HHV> branch distribution piping system shall have the ability to connect 2 to 6 indoor units.

#### The system shall be capable of performing continuous operation even when power is turned off to an individual indoor unit.

#### The outdoor unit shall be internally assembled, wired and piped from the factory.

#### The factory assembled system shall have the outdoor unit fitted with refrigerant strainer, check valves, oil separator, 4-way reversing valve, electronic expansion valve(s), high side and low side refrigerant charging ports, and a service port.  The <LMU480HV><LMU541HV> shall include a hot gas bypass valve; the <LMU601HV><LMU361HHV><LMU421HHV><LMU480HHV> shall include a sub-cooled heat exchanger, vapor injection and vapor bypass circuit.

### Field Supplied Refrigerant Piping Design Parameters

#### The outdoor unit shall be capable of operating at an elevation of 98.4 feet above or below the indoor units.

#### The outdoor unit shall be capable of operating with up to 475 feet of total equivalent refrigerant piping length.

#### The outdoor unit shall be capable of operating with up to 229.6 equivalent feet of refrigerant piping length to the farthest indoor unit.

#### The piping length from BD unit to indoor unit shall not exceed 49.2 equivalent feet.

#### The elevation difference between BD unit and indoor unit, above or below BD unit, shall not exceed 32.8 feet.

#### The elevation difference between two parallel BD units shall not exceed 49.2 feet.

### Defrost Operations

#### The outdoor unit shall be capable of auto defrost operation to melt accumulated ice off the outdoor unit heat exchanger. The defrost cycle control shall be based on outdoor ambient temperatures and outdoor unit heat exchanger temperatures.

#### The <LMU481HV><LMU541HV><LMU601HV> shall accommodate an optional drain pan heater.  The <LMU361HHV><LMU421HHV><LMU480HHV> shall include a factory installed drain pan heater.

### Oil Management

#### The outdoor unit scroll compressor shall utilize a high pressure oil sump to maintain oil quality and pressure differential, not an oil pump, to ensure a consistent film of oil on all moving compressor parts at low speed.

#### The outdoor unit scroll compressor shall have an oil separator and utilize centrifugal oil return to separate oil mixed with the refrigerant gas during compression and return oil to the compressor

### Fan and Motor Assembly

#### Each outdoor unit shall be equipped with two direct drive variable speed propeller fans with BLDC motors with a horizontal air discharge.

#### The fan blades shall be made of Acrylonitrile Butadiene Styrene (ABS) material.

#### The fan(s) shall be equipped with permanently lubricated bearings.

#### The fan motor(s) shall have variable speed to a maximum of 750 RPM <LMU601HV><LMU361HHV><LMU421HHV><LMU480HHV> or 670 RPM <LMU481HV><LMU541HV>.

#### The fan(s) shall have a raised guard to help prevent contact with moving parts.

### Cabinet

#### The outdoor unit cabinet shall be made of pre-coated metal (PCM).

#### The front/side panels of the outdoor unit shall be removable type for access to internal components.

#### Outdoor unit cabinet shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.

### Outdoor Unit Coil

#### The outdoor unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### The aluminum fins shall have factory applied corrosion resistant GoldFin™   material.

#### Coil coating shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.

#### The outdoor unit coil shall be factory tested to a pressure of 600 psig.

#### The coil for each outdoor unit shall have a minimum of 14 Fins per Inch (FPI).

#### The coil for each outdoor unit shall have a 2 row heat exchanger <LMU481HV><LMU541HV> or 3 row heat exchanger <LMU601HV><LMU361HHV><LMU421HHV><LMU480HHV>.

#### The coil for the <LMU601HV><LMU361HHV<LMU421HHV><LMU480HHV> outdoor unit shall have a vapor bypass circuit to separate gas refrigerant and return it to the compressor suction.

#### The outdoor unit cabinet shall have a coil guard.

### Compressor(s)

#### The outdoor unit shall be equipped with one hermetically sealed, digitally controlled, inverter driven scroll compressor with suction inlet directly into the compression chamber.

#### The inverter driven, digitally controlled compressor shall be capable of operating in a frequency range from 10 Hz to 150 Hz <LMU601HV><LMU361HHV><LMU421HHV><LMU480HHV> or 10 Hz to 130 Hz <LMU481HV><LMU541HV> with control in 1 Hz increments.

#### The compressor for the <LMU601HV><LMU361HHV<LMU421HHV><LMU480HHV> outdoor unit shall include vapor injection.

#### The compressor shall be mounted on vibration attenuating rubber grommets.

#### The compressor shall use a factory charge of Polyvinyl Ether (PVE) oil.

#### The compressor bearing(s) shall have Teflon™ coating.

#### The compressor shall be equipped with over-current protection.

### Operational Sound Levels

#### The outdoor unit shall have sound levels not exceeding 55 dB(A) <LMU361HHV><LMU481HV><LMU541HV>, 56 dB(A) <LMU421HHV><LMU480HHV>, or 58 dB(A) <LMU601HV> tested in an anechoic chamber under ISO 3745 standard.

### Sensors

#### The outdoor unit shall have

##### Suction temperature sensor

##### Discharge temperature sensor

##### High pressure sensor

##### Low pressure sensor

##### Outdoor temperature sensor

##### Outdoor unit heat exchanger temperature sensor

### Wind Load Installations for Outdoor Units

#### Provide Florida wind Load Installation Drawings that meet the requirements of the 2020 Florida Building Code, 7th Edition and ASCE Standard 7-2016 with submittal.

### Warranty

#### Limited Warranty Period

##### STANDARD FIVE (5) YEAR WARRANTY FOR A QUALIFIED SYSTEM - The Part(s) of a qualified System, including the compressor, are warranted for a period (the “Standard Parts Warranty Period”) ending five (5) years after the date of original installation. In absence of proof of installation the warranty date will end five (5) years from the date of manufacture.

##### ADDITIONAL TWO (2) YEAR COMPRESSOR PART WARRANTY - The Compressor is warranted for an additional two (2) year period after the end of the applicable Standard Part Warranty Period (the “Compressor Warranty Period”).

#### Extended Warranty

##### The Standard Warranty Period and the Compressor Warranty Period are extended to a total of ten (10) years (the “Extended Warranty Period”) for qualified Systems that have been (a) installed by a party that has completed the Training Requirements, (b) installation is pursuant to LG’s published instructions, and (c) product is registered within 60 days of startup at www.lg-dfs.com or www.lg-dfs-warranty.com.

## PRODUCT(S) - Branch Distribution Unit (Multi F Max Systems Only) <PMBD3620> <PMBD3630><PMBD3640><PMBD3641>

### Operating Range

#### The BD unit shall be capable of the following ambient operating range

##### 0°F DB to 150°F DB

### General

#### BD unit is designed for the use with Multi F MAX <LMU481HV><LMU541HV><LMU601HV> and Multi F MAX with LGRED° <LMU361HHV><LMU421HHV><LMU480HHV> outdoor units as manufactured by LG.

#### BD unit casing shall be galvanized steel.

#### BD unit shall require 208-230V/1-phase/60Hz power supply.

#### BD Unit shall be an intermediate refrigerant control device between the outdoor unit and the indoor units to effectively and efficiently control the heating or cooling operation of the Multi F MAX system.

#### BD unit shall have a two pipe system comprising of

##### Vapor pipe

##### Liquid Pipe

#### BD unit shall have 2, 3 or 4 ports.

#### Port capacity for <PMBD3620~PMBD3640> BD Units

##### Each port shall connect to 1 indoor unit for a maximum nominal capacity of 24MBh.

#### Port capacity for <PMBD3641> BD Unit

##### Ports A~C shall each connect to 1 indoor unit for a maximum nominal capacity of 24MBh.

##### Port D shall connect to 1 indoor unit for a nominal capacity of 24Mbh or 36MBh.

#### Maximum nominal capacity per BD unit shall not exceed 73MBh.

#### BD unit shall be internally piped, wired, assembled and run tested at the factory.

#### BD unit shall be designed for indoor installation.

#### BD unit shall have 2 two-positioned solenoid valves per port.

#### BD unit shall not require a condensate drain.

#### BD unit shall be internally insulated.

#### All field refrigerant lines from outdoor unit to BD unit and from BD unit to indoor units shall be field insulated.

#### BD unit shall not exceed a net weight of 16 lbs.

#### Two BD units shall be capable of being piped in parallel using an accessory Y-branch kit.

### Controls

#### BD unit shall have factory installed control boards and integral microprocessor to communicate with the main control board in the outdoor unit.

#### BD unit shall be connected to the outdoor unit and indoor units in a power/control circuit from outdoor units and to Indoor units using a minimum 14 AWG, 4 conductor, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### BD unit may be connected to optional field supplied and field installed isolation valves to isolate the BD unit for servicing without evacuating the entire system.

### Warranty

#### Limited Warranty Period

##### STANDARD FIVE (5) YEAR WARRANTY FOR A QUALIFIED SYSTEM - The Part(s) of a qualified System, including the compressor, are warranted for a period (the “Standard Parts Warranty Period”) ending five (5) years after the date of original installation. In absence of proof of installation the warranty date will end five (5) years from the date of manufacture.

##### ADDITIONAL TWO (2) YEAR COMPRESSOR PART WARRANTY - The Compressor is warranted for an additional two (2) year period after the end of the applicable Standard Part Warranty Period (the “Compressor Warranty Period”).

#### Extended Warranty

##### The Standard Warranty Period and the Compressor Warranty Period are extended to a total of ten (10) years (the “Extended Warranty Period”) for qualified Systems that have been (a) installed by a party that has completed the Training Requirements, (b) installation is pursuant to LG’s published instructions, and (c) product is registered within 60 days of startup at www.lg-dfs.com or www.lg-dfs-warranty.com.