Guide Specifications

## Wall Mounted – Standard <ARNU053SJA4><ARNU073SJA4><ARNU093SJA4> <ARNU123SJA4><ARNU153SJA4><ARNU183SKA4><ARNU243SKA4><ARNU303SVA4> <ARNU363SVA4>

### General

#### Unit shall be manufactured by LG.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be attached to an installation plate/bracket that secures unit to the wall.

#### The depth of the unit shall not exceed 8.25 inches.

### Casing/Panel

#### Unit case shall be manufactured using Acrylonitrile Butadiene Styrene (ABS) polymeric resin and has a pearl white finish designed for mounting on a vertical surface and includes an installation mounting template and hanging bracket.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet with a manual or motorized sweeping guide vane that automatically changes the direction of airflow from side-to-side and up-and-down.

#### Unit shall be equipped with factory installed temperature thermistors for:

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a factory assembled, piped and wired electronic expansion valve (EEV) for refrigerant control.

#### Unit shall have a built-in control panel to communicate with other indoor units and to the outdoor unit.

#### Unit shall have the following functions as standard:

##### Self-diagnostic function

##### Auto addressing

##### Auto restart function

##### Auto changeover function (Heat Recovery system only)

##### Auto operation function

##### Auto clean function

##### Child lock function

##### Forced operation

##### Dual thermistor control

##### Sleep mode

##### Dual set point control

##### Filter life timer

##### External on/off control input

##### Wi-Fi compatible

##### Auto fan operation

##### Refrigerant Refrigerant Leak detection logic

#### Unit shall be capable of refrigerant piping in four different directions.

#### Unit shall be capable of drain piping in two different directions.

### Fan Assembly

#### The unit shall have a single, direct driven crossflow tangential Sirocco fan made of high strength ABS BSN-7530 polymeric resin.

#### The fan impeller shall be statically and dynamically balanced.

#### The fan motor is Brushless Digitally commutated (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan motor shall include thermal, overcurrent and low RPM protection.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm that provides a minimum of three pre-programed fan speeds in the heating mode and fan only mode and four speeds in the cooling mode. The fan speed algorithm provides a field selectable fixed speed.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.

### Filter Assembly

#### The return air inlet shall have a factory supplied removable, washable filter

#### The filter access shall be from the front of the unit without the need of tools.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### The copper tubing shall have inner grooves to expand the refrigerant contact surface for high efficiency heat exchanger operation.

#### Unit shall have a minimum two row coil, 18 fins per inch.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of EPS (expandable polystyrene resin).

#### Unit shall be designed for gravity drain.

#### Unit shall have a 5/8” inside diameter factory insulated drain hose to handle condensate.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 550 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated. Each pipe should be insulated separately.

#### Thickness and heat transfer characteristics shall be determined by the design engineer and shall meet all code requirements.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system with or without the use of a wall mounted zone controller. The unit shall have a factory mounted return air thermistor for use as a space temperature control device. All operating parameters except scheduling shall be stored in non-volatile memory resident on the microprocessor. The microprocessor shall provide the following functions, self-diagnostics, auto re-start after a power failure and a test run mode.

#### The unit shall be able to communicate with other indoor units and the outdoor unit using a field supplied minimum of 18 AWG, two core stranded, twisted, and shielded communication cable (RS-485).

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover (Heat Recovery System only)

##### Heating

##### Cooling

##### Dry

##### Fan only

#### The unit shall be able to operate in either cooling or heating mode for testing and/or commissioning.

#### The unit shall be able to operate with the fan turned off during system cooling thermal off.

#### The unit shall have adjustable, multi-step cooling and heating mode thermal on/off temperature range settings.

#### The system shall include a product check function to access and display indoor unit type and capacity from a wired programmable thermostat controller.

#### Unit shall have a field settable method to choose auto fan speed change operation based on mode of operation, on/off fan operation based on mode of operation, or continuous minimum set fan speed operation.

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph./Hz).

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Controls

#### Unit shall use controls provided by the manufacturer to perform all functions necessary to operate the system effectively and efficiently and communicate with the outdoor unit over an RS485 daisy chain.

### Seismic Installations

#### Provide with submittal: 1) OSHPD Special Seismic Certification Preapproval (OSP) documents for certified product list of VRF equipment to be installed in high seismic risk areas. 2) Equipment installation documents in conformance with CBC 2013, 2016 and 2019 California Building Code and IBC 2012, 2015 and 2018 International Building Code.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.

#### warranty.