Guide Specifications

## Single Zone Heat Pump and Single Zone with LGRED° Heat Pump Indoor Unit (Ducted – High Static) <LHN248HV><LHN368HV><LHN428HV><LHN488HV>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 57°F WB to 77°F WB

##### Heating: 59°F DB to 81°F DB

### General

#### The unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped, and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be designed to mount fully concealed above the finished ceiling.

#### Unit shall have opening to supply air from front horizontal and a dedicated rear horizontal return.

#### The supply air opening shall be flanged for field installed ductwork that shall not exceed the external static pressure limitation of the unit.

#### The indoor units have sound ratings no higher than 42 dB(A) as tested per ISO Standard 3745.

#### The unit <LHN248HV><LHN368HV> shall be compatible with both standard single zone and LGRED° 24,000Btu/h and 36,000 Btu/h outdoor units in addition to Multi Zone outdoor units.

#### The unit <LHN428HV><LHN488HV> shall only be compatible with LGRED° <LUU420HHV><LUU480HHV>outdoor units.

### Casing/Panel

#### Unit case shall be manufactured using galvanized steel plate.

#### The cold surfaces of the unit shall be covered internally with a coated polystyrene insulating material.

#### The cold surfaces of the unit shall be covered externally with sheet insulation made of Ethylene Propylene Diene Monomer (M-Class) (EPDM).

#### The external insulation shall be plenum rated and conform to ASTM Standard D-1418.

#### Unit shall be provided with hanger brackets designed to support the unit weight on four corners.

#### Hanger brackets shall have pre-punched holes designed to accept field supplied, all thread rod hangers.

### Cabinet Assembly

#### Unit shall have supply air discharge outlets horizontal and a return air inlet horizontal.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto changeover function

##### Dehumidifying function

##### Child lock function

##### Dual thermistor control

##### Hot Start

##### Sleep mode

##### External static pressure (ESP) control

### Fan Assembly

#### The unit shall have two direct driven Sirocco fans.

#### The fan shall be made of high strength ABS GP-2200 polymeric resin.

#### The fans shall be mounted on a common shaft.

#### The fan motor shall be Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using a microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.

#### The Auto fan setting shall adjust the fan speed to achieve the set-point most effectively.

#### Each of the settings can be field adjusted from the factory setting (RPM/ESP).

##### Unit <LHN248HV> <LHN368HV> manufactured starting October 2020, <LHN428HV> <LHN488HV> upon launch, shall have Auto ESP Control to adjust and deliver constant airflow regardless of permitted external static pressure.

#### Unit shall be designed for high-speed air volume against an external static pressure of up to 0.59 inches water gauge <LHN248HV> <LHN368HV><LHN428HV> <LHN488HV>.

### Filter Assembly

#### The return air inlet shall have a factory supplied removable, washable filter.

#### The filter access shall be from the rear of the unit.

#### <Optional><Return filter box with high-efficiency filter shall be field provided and installed not to exceed external static pressure limitation of the high static ducted indoor unit.>

##### <The unit shall have provision to mate directly with high efficiency filter box to accommodate 1” or 2” thick field provided MERV rated filter.>

### Coil Assembly

#### Unit shall have a factory-built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 3 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil.

#### Unit shall have an installed and wired condensate drain pump capable of providing minimum 27.5-inch lift from bottom surface of the unit.

#### The drain pump shall have a safety switch to shut off the unit if condensate rises too high in the drain pan.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 551 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### The unit shall be able to communicate with the outdoor unit using a field supplied minimum of 14 AWG, 4 conductors, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through an optional control board for the outdoor unit.

#### Group control shall be available to allow multiple indoor units to operate from a single controller or allow connection of more than one controller to an indoor unit.

#### The unit shall be able to operate with the fan turned off during system cooling thermal off.

#### The unit shall be able to operate with a continuous fan setting.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Controls

#### The indoor unit shall use controls provided by the manufacturer to perform all functions necessary to operate the system effectively and efficiently.

#### An optional wireless handheld controller shall be available as an additional accessory for use with installed LG wired controller.

#### An optional dry contact shall be available as an additional accessory.

#### The indoor unit shall accommodate an optional Wi-Fi module as an additional accessory to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.