Guide Specifications

Single Zone Systems – Wall Mounted (Outdoor and Indoor Units)

- GENERAL

  - Basis of Design Shall be LG

    - Acceptable standards shall be supplied based upon the performance characteristics and features of the LG model number(s) specified, LG model families specified, and as otherwise specified herein. Alternate suppliers shall request permission to bid, in writing, from the engineer at least 10 days prior to the bid date. This request by the contractor to bid an alternate supplier to the basis of design, listed or not listed, shall not relieve the contractor of supplying all materials, options, controls, sequences, efficiencies and intents of the original specifications written or implied by LG model number or model family or as otherwise specified. The written request and engineers’ written response to such request shall be included in all submittal documents for approval.

  - Alternate Equipment Bid Instruction

    - The contractor shall provide basis of design bid as specified and with specified products. If the contractor should wish to propose any alternate products to the basis of designed products they shall provide a separate and complete Bid detailing the proposed alternate products and the associated adjustment of price to support the change from basis of design products. The contractor bids the alternate product with full knowledge that the proposed product may not be acceptable or approved. In no event shall the contractor be entitled to additional compensation to supply such specified products, options, sequences or intents. Any and all additional cost, to any party, because of any product submitted on or supplied other than that of the original specified products shall be the responsibility of the contractor without recourse. It is agreed that any and all disputes regarding any differences between the specified products, options, sequences or intents and that proposed as an alternate shall be arbitrated by the engineer of record. It shall be further agreed by all parties that all decisions of arbitration shall be final and binding. Any product proposed as an alternate shall have been offered, as a VRF product, in the United States for a minimum of (5) years.

  - System Performance Documentation

    - The manufacturer shall provide published outdoor unit performance data in table format which states the product heating and cooling capacities expressed in British thermal units per hour (BtuH) and power consumption expressed in kilowatts (kW) at a minimum of 8 possible combinations of allowed conditions between 50% and 130% connection ratio (VRF systems). Possible combinations of allowed condition variables include Combination Ratios expressed as a percentage value, Outdoor Ambient Temperature expressed in degrees Fahrenheit (°F), and indoor unit Entering Air wet and dry bulb temperature expressed in degrees Fahrenheit (°F). Any product whose system design and engineering manuals or guides where published data tables are expressed in units other than these specified will not be accepted.

    - Any product whose published documentation requires the design engineer to apply a correction factor derived from a published curve or tabular data for combination ratio, outdoor ambient temperature, and/or entering air temperature against rated conditions to obtain performance at any possible combination of allowed conditions will not be accepted.

  - Submittals

    - A complete submittal package shall be compiled and 10 copies shall be forwarded to the general contractor who shall supply the architect with the submittals for dissemination to all parties. The submittal shall be a collection of documents that represent the technical aspects of each product or collection of products to be used on the project. All performance submissions shall be calculated at the design temperatures, Nominal performance data shall not be accepted. The submission and approval of said submittals does not relieve the contractor of supplying all requirements set forth in the specification and drawings. Any substitutions offered by the contractor shall include, as a separate document, any and all differences between the submitted products and the specified products including but not limited to, all dimensions, electrical, control, weights, warranties, country of origin.

    - If submittals contain any proposed alternate equipment specifications, calculations, dimensions, electrical specifications, sound specifications or any other mandated submission which are not accepted, are noted or rejected for any reason the contractor shall be allowed to correct any deficiency and re-submit a second time. Should there be any irregularities found on second submission, the contractor will be directed to and agrees to submit on the original specified products, including any changes or revisions, and provide those specified products without any additional compensation.

  - Delivery, Storage and Handling

    - Provide a dry and clean place for the products. Comply with manufacturer’s instructions on handling to prevent products from damaging. If product is damaged upon arrival, reject the shipment. If hidden damage is found after removing the product from the container, retain container and all packing material. Contractor is responsible for filing a claim with the freight carrier.

  - Upon Job Completion

    - Provide the owner with an LG tablet containing a copy of approved submittal, LGMV Mobile (VRF system service diagnostics) software, project mechanical and control drawings, all as-built piping drawings, AHRI seismic certificates and Florida Wind Loads as required by state, installation, operation and maintenance manuals, troubleshooting guides, service manuals and engineering manuals in PDF format.

    - Provide the owner with an LG tablet containing a copy of the approved submittal package, a full set of drawings and specifications, on boarding software, custom documents, such as control drawings, shop drawings, wiring diagrams, BMS software, GUI image files, commissioning reports, refrigerant charge calculations, refrigerant piping design and as-built reports, O&M’s, troubleshooting guides, service manuals, and equipment engineering manuals in .pdf format. Tablet shall also include a licensed copy of deluxe version of the VRF equipment manufacturer’s service diagnostics.

- STANDARDS/CERTIFICATIONS

  - Certified Product Performance Ratings

    - All VRF (Variable Refrigerant Flow) and VSMS (Variable Speed Multi-Split and Mini- Split) products shall have published performance ratings certified by AHRI (Air-Conditioning, Heating, and Refrigeration Institute) and listed in the AHRI certified product directories available at www.ahridirectory.org.

  - Production Facility Certifications

    - All system components shall be manufactured in production facilities maintaining the following ISO certifications:

      - ISO 9001 Quality Management System

      - ISO 14001 Environmental Management System

  - UL Compliance

    - All system shall comply with Underwriters Laboratories (UL) 1995 5th edition of the Standard for Safety for Heating and Cooling Equipment Standard for Safety and bear the Electrical Testing Laboratories (ETL) and/or Canadian Standards Association (CSA) mark on the product name plate. Current withdrawal date set for December 31, 2023, where UL 60335-2-40 4th edition becomes effective January 1st, 2024.

  - Electrical Standard

    - All system electrical power wiring shall be installed in accordance with the NFPA 70 National Electrical Code (NEC) or applicable state and local building codes.

  - Corrosion Quality Control

    - Outdoor unit painted surfaces shall be factory tested for a minimum of 1000 hours using the accelerated salt spray test procedure as documented in ASTM Standard B-117 using the Surface Scratch Test Procedure. Photographic evidence shall be available upon request by the Engineer of Record.

    - Photographic evidence shall include images of the test sample showing the surface scratch area at zero (0) hours, 400 hours, and 1000 hours. Post-test images of the sample must show no significant deterioration of the coating material, blistering, flaking, peeling, or rust formation along the test scratch.

- Single Zone Heat Pump Systems – Wall Mounted

  - Single Zone Heat Pump Outdoor Unit (Wall Mounted)

  - Single Zone Heat Pump Indoor Units (Wall Mounted – Art Cool Premier)

  - Single Zone Heat Pump Indoor Units (Wall Mounted - Art Cool Mirror

  - Single Zone Heat Pump Indoor Units (Wall Mounted – High Efficiency)

  - Single Zone Heat Pump Indoor Units (Wall Mounted - Long Pipe)

  - Single Zone Heat Pump Indoor Units (Wall Mounted – Mega, Standard Efficiency)

## Single Zone Heat Pump Outdoor Unit (Wall Mounted) <LSU090HXV2><LSU120HXV2><LSU090HEV2><LSU120HEV2><LSU180HEV2><LSU240HEV2><LSU090HFV3><LSU120HFV3><LSU180HFV3><LSU240HFV3><LAU090HYV3><LAU120HYV3><LAU150HYV3><LAU180HYV3><LAU240HYV3><LSU090HSV5><LSU120HSV5><LSU181HSV5><LSU243HLV3><LSU303HLV3><LSU363HLV3>

### Product Design

#### The Single zone HVAC system shall be a variable capacity, direct expansion (DX) heat pump system consisting of a single outdoor unit and single indoor unit.  The outdoor unit shall have a single inverter compressor.  The outdoor unit shall be connected to the indoor unit with piping and control wiring.

#### The LG heat pump system shall be an air cooled system consisting of a single outdoor unit connected to a single indoor unit.

#### Single zone system requires the indoor unit to be piped with the outdoor unit to complete the refrigeration system

#### The heat pump system will be available in 208/230V, 60Hz, 1 phase or <the LS---HXV2 system will be available in 115V, 60Hz, 1 phase>.

### Operating Conditions

#### The outdoor unit shall be capable of the following ambient operating range.

##### <LAU---HYV3>

###### Cooling: 14°F DB to 118°F DB <with optional low ambient kit from 0°F DB to 118°F DB>

###### Heating: -13°F WB to 65°F WB

##### <LSU---HSV5, LSU---HLV3>

###### Cooling: 14°F DB to 118°F DB <with optional low ambient kit from 0°F DB to 118°F DB>

###### Heating: -4°F WB to 65°F WB

##### <LSU---HXV2><LSU---HEV2><LSU---HFV3>

###### Cooling: 14°F DB to 118°F DB

###### Heating: 14°F WB to 65°F WB

### General

#### Unit shall be manufactured by LG.

#### The air-conditioning system shall use R410A refrigerant.

#### The system shall have one air source outdoor unit.

#### The refrigerant circuit shall be field piped to a single matching indoor unit to effectively and efficiently control the heating or cooling operation of the system.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

#### Factory installed microprocessor controls in the outdoor unit and indoor unit shall perform functions to efficiently operate the single zone system and communicate via minimum 14 AWG, 4 conductor, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### The outdoor unit shall be internally assembled, wired and piped from the factory.

#### The factory assembled system shall have the outdoor unit fitted with refrigerant strainer, check valves, oil separator, accumulator, 4-way reversing valve, electronic expansion valve, high side and low side refrigerant charging ports, and a service port.

### Piping Capabilities

#### The outdoor unit shall be capable of operating at an elevation of 23 feet < LSU---HXV2, LSU090~120HEV2, LSU090~120HFV3>, 32.8 feet <LSU180~240HEV2, LSU180~240HFV3>, 39.4 feet <LAU090~120HYV3>, 49.2 feet <LSU---HSV5>, or 98.4 feet < LAU150~240HYV3, LSU---HLV3> above or below the indoor units.

#### The outdoor unit shall be capable of operating with up to 49.2 feet < LSU---HXV2, LSU090~120HEV2, LSU090~120HFV3>, 65.6 feet <LAU090~120HYV2, LSU180~240HEV2, LSU180~240HFV3>, 82 feet <LSU090~120HSV5>, 114.8 feet <LSU181HSV5>, or 164 feet <LAU150~240HYV3, LSU---HLV3> of total equivalent refrigerant piping length.

### Defrost Operations

#### The outdoor unit shall be capable of auto defrost operation to melt accumulated ice off the outdoor unit heat exchanger. The defrost cycle control shall be based on outdoor ambient temperatures and outdoor unit heat exchanger temperatures.

#### The <LAU---HYV3>, <LSU---HLV3>, and <LSU090,120,181HSV5> outdoor units shall be equipped with a factory installed drain pan heater.

### Oil Management

#### The outdoor unit shall have an oil injection mechanism to ensure a consistent film of oil on all moving compressor parts at low speed.

#### The outdoor unit shall have an oil separator to separate oil mixed with the refrigerant gas during compression and return oil to the compressor.

### Cabinet

#### The outdoor unit cabinet shall be made of pre-coated metal (PCM).

#### The front/side panels of the outdoor unit shall be removable type for access to internal components.

#### Outdoor unit cabinet shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.

### Fan Assembly

#### The outdoor unit shall be equipped with one direct drive variable speed propeller fan with Brushless Digitally Controlled (BLDC) motor with a horizontal air discharge.

#### The fan blades shall be made of Acrylonitrile Butadiene Styrene (ABS) material.

#### The fan shall be equipped with permanently lubricated bearings.

#### The fan motor shall have variable speed to a maximum of 950 RPM.

#### The fan shall have a raised guard to help prevent contact with moving parts.

### Outdoor Coil

#### The outdoor unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### The aluminum fins shall have factory applied corrosion resistant GoldFin™   material.

#### Coil coating shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.

#### The outdoor unit coil shall be factory tested to a pressure of 600 psig.

#### The coil for each outdoor unit shall have a minimum of 14 Fins per Inch (FPI).

#### The coil for each outdoor unit shall have a 2 row heat exchanger.

#### The outdoor unit cabinet shall have a coil guard.

### Compressor

#### Each outdoor unit shall be equipped with one hermetically sealed, digitally controlled, inverter driven twin-rotary compressor with vibration isolation.

#### The inverter driven, digitally controlled compressor shall be capable of operating throughout its frequency range with control in 1 Hz increments.

#### The compressor shall be mounted on vibration attenuating rubber grommets.

#### The compressor shall use a factory charge of Polyvinyl Ether (PVE) oil.

#### The compressor bearing(s) shall have Teflon™ coating.

#### The compressor shall be equipped with over-current protection.

### Sound Levels

#### The outdoor unit shall have sound levels not exceeding 58 dB(A) tested in an anechoic chamber under ISO 3745 standard.

### Sensors

#### The outdoor unit shall have

#### Suction temperature sensor

#### Discharge temperature sensor

#### High pressure sensor

#### Low Pressure sensor

#### Outdoor temperature sensor

#### Outdoor unit heat exchanger temperature sensor

### Wind Load Installations for Outdoor Units

#### Provide Florida wind Load Installation Drawings that meet the requirements of the 2020 Florida Building Code, 7th Edition and ASCE Standard 7-2016 with submittal

### Warranty

#### Limited Warranty Period

##### STANDARD FIVE (5) YEAR WARRANTY FOR A QUALIFIED SYSTEM - The Part(s) of a qualified System, including the compressor, are warranted for a period (the “Standard Parts Warranty Period”) ending five (5) years after the date of original installation. In absence of proof of installation the warranty date will end five (5) years from the date of manufacture.

##### ADDITIONAL TWO (2) YEAR COMPRESSOR PART WARRANTY - The Compressor is warranted for an additional two (2) year period after the end of the applicable Standard Part Warranty Period (the “Compressor Warranty Period”).

#### Extended Warranty

##### The Standard Warranty Period and the Compressor Warranty Period are extended to a total of ten (10) years (the “Extended Warranty Period”) for qualified Systems that have been (a) installed by a party that has completed the Training Requirements, (b) installation is pursuant to LG’s published instructions, and (c) product is registered within 60 days of startup at www.lg-dfs.com or www.lg-dfs-warranty.com.

## Single Zone Heat Pump Indoor Units (Wall Mounted – Art Cool Premier) <LAN090HYV3><LAN120HYV3><LAN150HYV3><LAN180HYV3><LAN240HYV3>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 53°F WB to 75°F WB

##### Heating: 60°F DB to 86°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be attached to an installation plate/bracket that secures unit to the wall.

#### The depth of the unit shall not exceed 10-1/2 inches.

### Casing/Panel

#### Unit casing shall be manufactured of heavy duty Acrylonitrile Butadiene Styrene (ABS) and High Impact Polystyrene (HIPS) plastic.

#### Unit case shall have a pearl white finish: Munsell 7.5BG 10/2 (RAL 9016).

#### The front surface of the unit shall have an architectural curved panel with pearlized patterned finish.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto changeover function

##### Auto clean function

##### Dehumidifying function

##### Hot Start

##### Sleep mode

#### Unit shall be capable of refrigerant piping in 4 different directions.

#### Unit shall be capable of drain piping in 2 different directions.

### Fan Assembly

#### The unit shall have a direct drive, cross flow fan made of high strength ABS plastic.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, Power Heat, and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.

### Filter Assembly

#### The return air inlet shall have a factory supplied primary removable, washable filter.

#### The filter access shall be from the front of the unit.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 2 rows <LAN090~120HYV3> or 3 rows <LAN150~240HYV3> of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).

#### Unit shall be designed for gravity drain.

#### Unit shall have a factory insulated drain hose to handle condensate.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 551 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### The unit shall be able to communicate with the outdoor unit using a field supplied minimum of 14 AWG, 4 conductor, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### The unit shall be capable of setting Cooling Only operation.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Condensate Sensor Connection

#### The unit shall include a factory installed condensate sensor connection compatible with the AquaGuard® AG-9300-LG condensate sensor.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory.

#### The unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.

## Single Zone Heat Pump Indoor Units (Wall Mounted - Art Cool Mirror) <LAN090HSV5><LAN120HSV5><LAN181HSV5>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 53°F WB to 75°F WB

##### Heating: 60°F DB to 86°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be attached to an installation plate/bracket that secures unit to the wall.

#### The depth of the unit shall not exceed 9 inches.

### Casing/Panel

#### Unit casing shall be manufactured of heavy duty Acrylonitrile Butadiene Styrene (ABS) and High Impact Polystyrene (HIPS) plastic.

#### Unit case shall have a jet black finish: Munsell 7.5PB 0.2/20 (RAL 9005).

#### The front surface of the unit shall have an architectural flat panel with smoked charcoal mirror finish and integrated digital display.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto changeover function

##### Auto clean function

##### Dehumidifying function

##### Hot Start

##### Sleep mode

#### Unit shall be capable of refrigerant piping in 4 different directions.

#### Unit shall be capable of drain piping in 2 different directions.

### Fan Assembly

#### The unit shall have a direct drive, cross flow fan made of high strength ABS plastic.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, Power Heat, and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.

### Filter Assembly

#### The return air inlet shall have a factory supplied primary removable, washable filter.

#### The unit shall be equipped with factory supplied secondary 3M Micro Dust filter.

#### The filter access shall be from the front of the unit.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 2 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).

#### Unit shall be designed for gravity drain.

#### Unit shall have a factory insulated drain hose to handle condensate.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 551 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### The unit shall be able to communicate with the outdoor unit using a field supplied minimum of 14 AWG, 4 conductor, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through an optional control board for the outdoor unit.

#### The unit shall be capable of setting Cooling Only and Heating Only operation.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Condensate Sensor Connection

#### The unit shall include a factory installed condensate sensor connection compatible with the AquaGuard® AG-9300-LG condensate sensor.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory.

#### The unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.

## Single Zone Heat Pump Indoor Units (Wall Mounted – High Efficiency) <LSN090HSV5><LSN120HSV5><LSN181HSV5>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 53°F WB to 75°F WB

##### Heating: 60°F DB to 86°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be attached to an installation plate/bracket that secures unit to the wall.

#### The depth of the unit shall not exceed 9 inches.

### Casing/Panel

#### Unit case shall be manufactured of heavy duty Acrylonitrile Butadiene Styrene (ABS) and High Impact Polystyrene (HIPS) plastic.

#### Unit case shall have a pearl white finish: Munsell 7.5BG 10/2 (RAL 9016).

#### The front surface of the unit shall have an architectural curved panel with pearl white finish and integrated digital display.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto changeover function

##### Auto clean function

##### Dehumidifying function

##### Hot Start

##### Sleep mode

#### Unit shall be capable of refrigerant piping in 4 different directions.

#### Unit shall be capable of drain piping in 2 different directions.

### Fan Assembly

#### The unit shall have a direct drive, cross flow fan made of high strength ABS plastic.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, Power Heat, and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.

### Filter Assembly

#### The return air inlet shall have a factory supplied primary removable, washable filter.

#### The unit shall be equipped with factory supplied secondary 3M Micro Dust Filter.

#### The filter access shall be from the front of the unit.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 2 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).

#### Unit shall be designed for gravity drain.

#### Unit shall have a factory insulated drain hose to handle condensate.

#### Unit shall have provision of 45° flare refrigerant pipe connections

#### The coil shall be factory pressure tested at a minimum of 551 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### The unit shall be able to communicate with the outdoor unit using a field supplied minimum of 14 AWG, 4 conductor, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through an optional control board for the outdoor unit.

#### The unit shall be capable of setting Cooling Only and Heating Only operation.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Condensate Sensor Connection

#### The unit shall include a factory installed condensate sensor connection compatible with the AquaGuard® AG-9300-LG condensate sensor.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory.

#### The unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.

## Single Zone Heat Pump Indoor Units (Wall Mounted - Long Pipe) <LSN243HLV3> <LSN303HLV3><LSN363HLV3>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 53°F WB to 75°F WB

##### Heating: 60°F DB to 86°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be attached to an installation plate/bracket that secures unit to the wall.

#### The depth of the unit shall not exceed 10-1/2 inches.

### Casing/Panel

#### Unit casing shall be manufactured of heavy duty Acrylonitrile Butadiene Styrene (ABS) and High Impact Polystyrene (HIPS) plastic.

#### Unit case shall have a pearl white finish: Munsell 7.5BG 10/2 (RAL 9016).

#### The front surface of the unit shall have an architectural flat panel with pearl white finish.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto changeover function

##### Auto clean function

##### Dehumidifying function

##### Hot Start

##### Sleep mode

#### Unit shall be capable of refrigerant piping in 4 different directions.

#### Unit shall be capable of drain piping in 2 different directions.

### Fan Assembly

#### The unit shall have a direct drive, cross flow fan made of high strength ABS plastic.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, Power Heat, and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.

### Filter Assembly

#### The return air inlet shall have a factory supplied primary removable, washable filter.

#### The filter access shall be from the front of the unit.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 2 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).

#### Unit shall be designed for gravity drain.

#### Unit shall have a factory insulated drain hose to handle condensate.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 551 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### The unit shall be able to communicate with the outdoor unit using a field supplied minimum of 14 AWG, 4 conductor, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through an optional control board for the outdoor unit.

#### The unit shall be capable of setting Cooling Only operation.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Condensate Sensor Connection

#### The unit shall include a factory installed condensate sensor connection compatible with the AquaGuard® AG-9300-LG condensate sensor.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory.

#### The unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.

## Single Zone Heat Pump Indoor Units (Wall Mounted – Mega, Standard Efficiency) <LSN090HXV2><LSN120HXV2><LSN090HEV2><LSN120HEV2><LSN180HEV2><LSN240HEV2>
<LSN090HFV3><LSN120HFV3><LSN180HFV3><LSN240HFV3>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 53°F WB to 75°F WB

##### Heating: 60°F DB to 86°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be attached to an installation plate/bracket that secures unit to the wall.

#### The depth of the unit shall not exceed 10 inches.

### Casing/Panel

#### Unit case shall be manufactured of heavy duty Acrylonitrile Butadiene Styrene (ABS) and High Impact Polystyrene (HIPS) plastic.

#### Unit case shall have a pearl white finish: Munsell 7.5BG 10/2 (RAL 9016).

#### The front surface of the unit shall have an architectural curved panel with pearl white finish and integrated digital display.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto changeover function

##### Auto clean function

##### Dehumidifying function

##### Hot Start

##### Sleep mode

#### Unit shall be capable of refrigerant piping in 4 different directions.

#### Unit shall be capable of drain piping in 2 different directions.

### Fan Assembly

#### The unit shall have a direct drive, cross flow fan made of high strength ABS plastic.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, Power Heat and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed manual guide vane to adjust the direction of flow of air from side to side.

### Filter Assembly

#### The return air inlet shall have a factory supplied removable, washable filter.

#### The filter access shall be from the front of the unit.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 2 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).

#### Unit shall be designed for gravity drain.

#### Unit shall have a factory insulated drain hose to handle condensate.

#### Unit shall have provision of 45° flare refrigerant pipe connections

#### The coil shall be factory pressure tested at a minimum of 551 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### The unit shall be able to communicate with the outdoor unit using a field supplied minimum of 14 AWG, 4 conductor, stranded, shielded or unshielded power/communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### <The LSN---HEV2 and LSN---HFV3 electrical power shall be 208-230/1/60 (V/Ph/Hz)> or <The LSN---HXV2 electrical power shall be 115/1/60 (V/Ph/Hz)>

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Condensate Sensor Connection

#### The unit shall include a factory installed condensate sensor connection compatible with the AquaGuard® AG-9300-LG condensate sensor.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory <LSN---HEV2 as of Aug 2019 production>

### Warranty

Please refer to the respective outdoor unit for applicable warranty.